HOLLISTER INCORPORATED

Digital Manufacturing Footprint

Solution Architecture & Baseline Configuration

From Manufacturing Line to Enterprise Supply Chain

Baseline Plant: Hollister Ballina, Co. Mayo, Ireland

Document Version: 1.0 DRAFT

Date: February 2026

Classification: CONFIDENTIAL

Prepared for Hollister Incorporated

Covering: Sensors, PLCs, DCS, Compute, Storage, Network, Metrology,

cGMP Compliance, V&V, Manufacturing on Demand, and Interim PLM

# Table of Contents

Table of Contents	2

1. Executive Summary	3

2. Design Principles & Architectural Framework	4

2.1 Governing Principles	4

2.2 ISA-95 / Purdue Model Alignment	4

2.3 Hierarchical Scope Model	5

3. Baseline Plant Configuration: Ballina, Ireland	6

3.1 Plant Profile & Assumptions	6

3.2 Baseline Manufacturing Line Architecture	6

4. Programmable Logic Controller (PLC) Configuration	8

4.1 PLC Strategy & Vendor Recommendation	8

4.1.1 Primary PLC Platform: Rockwell Automation Allen-Bradley	8

4.1.2 Secondary PLC Platform: Siemens (Interoperability Layer)	8

4.2 PLC Allocation per Manufacturing Line	8

4.3 PLC Configuration per Plant (Full Deployment)	9

4.4 PLC Network Architecture	9

4.5 PLC Programming Standards	10

5. Distributed Control System (DCS) Configuration	11

5.1 DCS Strategy	11

5.1.1 Recommended Platform: Rockwell PlantPAx	11

5.2 DCS Scope per Manufacturing Line	11

5.3 DCS Architecture per Plant	11

5.4 DCS Redundancy & High Availability	12

6. Comprehensive Sensor Architecture	13

6.1 Sensor Strategy Overview	13

6.2 Manufacturing Equipment Sensors (Vendor-Specific)	13

6.2.1 Station S2: Forming/Molding — Highest Sensor Density	13

6.2.2 Station S5: Inspection/Testing — Highest Precision	13

6.3 Common Sensors (Standardized Across All Plants)	14

6.3.1 Environmental Monitoring (Clean Room & Controlled Areas)	14

6.3.2 Utility Monitoring	14

6.3.3 Machine Health / Predictive Maintenance	15

6.4 Camera Systems	16

6.4.1 Machine Vision Cameras (Quality / Inspection)	16

6.4.2 Process Monitoring Cameras	16

6.4.3 Facility Security Cameras	16

7. Human Activity Monitoring	18

7.1 Scope & Ethical Framework	18

7.2 Monitoring Technologies	18

8. IoT, Compute, Storage & Network Infrastructure	19

8.1 IoT Gateway Architecture	19

8.2 On-Premise Compute Infrastructure	19

8.2.1 Server Room Configuration (per Plant)	19

8.2.2 Cloud Extension (Off-Site Compute)	19

8.3 Network Architecture	20

8.3.1 Network Segmentation (ISA-95 Aligned)	20

8.3.2 Network Bandwidth & Redundancy	21

9. Metrology, Calibration & Measurement Assurance	22

9.1 Metrology Strategy	22

9.2 Calibration Management System	22

9.3 Measurement Assurance Program	22

10. Qualification Framework: IQ/OQ/PQ & V&V	23

10.1 Qualification Strategy	23

10.2 Qualification Scope per Component Category	23

10.3 V&V for Systems Engineering	24

11. Manufacturing on Demand (MOD) Accommodations	25

11.1 MOD Architecture Requirements	25

11.2 Recipe-Driven Production	25

11.3 Rapid Changeover Support	25

11.4 Dynamic Resource Allocation	25

12. Interim PLM Solution	26

12.1 Interim PLM Strategy	26

12.2 Interim PLM Platform Recommendation	26

12.2.1 Primary Recommendation: Aras Innovator (Open Source Core)	26

12.2.2 Alternative: SharePoint-Based PLM Lite (Lower Capability)	26

12.3 Interim PLM Functional Scope	26

12.4 PLM-MES Integration (Critical Interface)	27

13. Technology Transfer & Change Control	28

13.1 R&D to Manufacturing Tech Transfer	28

13.1.1 Design Transfer Package (Digital)	28

13.1.2 Digital Thread Continuity	28

13.2 Change Control Framework	28

13.3 Configuration Management	29

14. cGMP Compliance Architecture	30

14.1 Regulatory Mapping	30

14.2 Data Integrity (ALCOA+ Principles)	30

15. Cybersecurity Architecture	32

15.1 Defense-in-Depth Strategy	32

15.2 Identity & Access Management	32

16. Scaling Model: Line to Plant to Enterprise	33

16.1 Horizontal Scaling (Adding Lines)	33

16.2 Vertical Scaling (Plant Replication)	33

16.3 Enterprise Integration (Supply Chain)	33

17. Implementation Roadmap	35

17.1 Phased Deployment Plan	35

17.2 Investment Estimate (Order of Magnitude)	35

18. Appendices	37

Appendix A: Acronym Reference	37

Appendix B: Key Vendor Summary	38

# 1. Executive Summary

This Solution Architecture defines the complete digital manufacturing footprint for Hollister Incorporated, establishing a modular, scalable, and cGMP-compliant baseline configuration starting at the Ballina, Ireland plant. The architecture spans from individual sensor endpoints on manufacturing equipment to enterprise-wide supply chain integration, designed with the explicit goal of replicability across all Hollister global manufacturing facilities.

The design addresses six fundamental requirements: modularity (plug-and-play component architecture enabling graceful change introduction), scalability (from single manufacturing line to full enterprise), resilience (fault tolerance at every layer with no single points of failure), security (defense-in-depth aligned with IEC 62443 and FDA 21 CFR Part 11), precision (metrology-grade measurement traceability), and compliance (end-to-end V&V supporting IQ/OQ/PQ qualification and cGMP requirements).

A critical design constraint is the accommodation of an interim PLM solution that provides immediate value while maintaining clean migration paths to a permanent PLM platform when the organization is ready. Similarly, the architecture supports Manufacturing on Demand (MOD) through configurable production recipes, dynamic resource allocation, and rapid changeover capabilities.

Baseline Scope: One manufacturing line at the Ballina facility, fully instrumented and integrated, serving as the validated template for horizontal and vertical scaling across all Hollister plants globally.

# 2. Design Principles & Architectural Framework

## 2.1 Governing Principles

Every design decision in this architecture is evaluated against the following non-negotiable principles, which reflect both operational excellence requirements and regulatory obligations inherent to medical device manufacturing.

| Principle | Description | Compliance Mapping |
| --- | --- | --- |
| Modularity | Each component (sensor, PLC, DCS module, compute node) is independently deployable, replaceable, and upgradeable without disrupting adjacent systems. | IEC 62443 Zone/Conduit, ISA-95 Levels |
| Scalability | Architecture scales horizontally (add lines, plants) and vertically (add analytics, AI layers) without re-architecture. | ISA-95 Enterprise Integration |
| Resilience | No single point of failure at any layer. Graceful degradation with automatic failover. Local autonomy preserved during WAN outages. | IEC 61508 SIL, FDA 21 CFR 211 |
| Security | Defense-in-depth: network segmentation, zero-trust, encrypted communications, role-based access, audit trails. | IEC 62443, FDA 21 CFR Part 11, GDPR |
| Precision | Metrology-grade measurement with traceability to international standards. Calibration management integrated into operations. | ISO 17025, FDA 21 CFR Part 211.68 |
| Compliance-by-Design | cGMP compliance, V&V, IQ/OQ/PQ built into every layer rather than bolted on. | FDA 21 CFR Parts 11/210/211/820, EU MDR Annex XIII |
| Change Control | Graceful introduction of change with full impact analysis, rollback capability, and validated state management. | GAMP 5, ICH Q10 |
| Interoperability | Open standards preferred (OPC-UA, MQTT, ISA-95 B2MML) to avoid vendor lock-in and enable ecosystem evolution. | ISA-95, IEC 62264, OPC-UA |

## 2.2 ISA-95 / Purdue Model Alignment

The architecture strictly follows the ISA-95 (Purdue) model for hierarchical separation of concerns. This is not merely a network segmentation strategy but a fundamental organizational principle governing data flow, latency requirements, and security boundaries.

| Level | Function | Hollister Implementation | Latency Req. |
| --- | --- | --- | --- |
| Level 0 | Physical Process (Sensors/Actuators) | Field instruments, temperature/pressure/flow sensors, vision systems, actuators | <1 ms |
| Level 1 | Basic Control (PLCs/Safety) | Allen-Bradley/Siemens PLCs, safety controllers, local HMIs | 1-10 ms |
| Level 2 | Area Supervisory (DCS/SCADA) | DCS per manufacturing line, SCADA for facility-wide monitoring, historian | 100 ms-1 s |
| Level 3 | Site Operations (MES/MOM) | Manufacturing Execution System, batch management, quality management | 1-30 s |
| Level 3.5 | DMZ / Industrial DMZ | Data diodes, protocol break, OPC-UA aggregation servers | N/A (security) |
| Level 4 | Enterprise (ERP/PLM/SCM) | SAP/Oracle ERP, interim PLM, supply chain management, analytics | Minutes-hours |
| Level 5 | Enterprise Network/Cloud | Multi-cloud analytics, digital twin, enterprise data lake | Variable |

## 2.3 Hierarchical Scope Model

The digital footprint is organized hierarchically to enable modular deployment and independent qualification:

- Manufacturing Station: Individual machine or work cell with its associated sensors, PLCs, and local compute

- Manufacturing Line: Collection of stations forming a complete production process for a product family

- Shop Floor: All manufacturing lines within a production area sharing common utilities and infrastructure

- Plant: Complete facility including all shop floors, warehousing, utilities, and site infrastructure

- Enterprise: All plants connected via supply chain integration, shared analytics, and unified governance

Each level in this hierarchy has its own qualification package (IQ/OQ/PQ), change control boundary, and data sovereignty model. The baseline configuration defined herein covers Levels 0-3 for a single manufacturing line, with integration points defined for Levels 3.5-5.

# 3. Baseline Plant Configuration: Ballina, Ireland

## 3.1 Plant Profile & Assumptions

The Hollister Ballina facility in Co. Mayo, Ireland serves as the baseline plant for this digital footprint. As a medical device manufacturing facility operating under both FDA and EU MDR regulatory frameworks, it represents the most stringent compliance requirements, making it an ideal baseline that will satisfy requirements for any subsequent plant deployment.

| Parameter | Baseline Assumption |
| --- | --- |
| Facility Type | Medical device manufacturing (ostomy, continence care, wound care products) |
| Regulatory Framework | FDA 21 CFR 210/211/820, EU MDR 2017/745, ISO 13485:2016 |
| Number of Manufacturing Lines (Initial) | 6-8 production lines (baseline config for 1 line) |
| Clean Room Classes | ISO 7 (Class 10,000) and ISO 8 (Class 100,000) per ISO 14644 |
| Operating Schedule | 24/7 continuous operations, 3 shifts |
| Environmental Zones | Controlled (clean rooms), Semi-controlled (packaging), Uncontrolled (warehouse/utilities) |
| Existing Infrastructure | Legacy PLCs (mix of vendors), limited historian, manual quality data collection |
| Network Backbone | Existing Ethernet to be upgraded to segmented industrial Ethernet |

## 3.2 Baseline Manufacturing Line Architecture

A single manufacturing line serves as the repeatable unit of deployment. The baseline line is assumed to consist of the following stations (adapted to Hollister product families):

| Station | Function | Key Equipment | Sensor Density |
| --- | --- | --- | --- |
| S1: Raw Material Prep | Material handling, blending, pre-treatment | Mixers, dispensers, material handling robots | Medium (12-18 sensors) |
| S2: Forming/Molding | Primary forming of product components | Injection molders, thermoformers, extruders | High (25-40 sensors) |
| S3: Assembly | Component assembly and sub-assembly | Pick-and-place, ultrasonic welders, adhesive dispensers | High (20-35 sensors) |
| S4: Coating/Treatment | Surface treatment, adhesive application | Coating systems, UV cure, drying ovens | High (20-30 sensors) |
| S5: Inspection/Testing | In-line quality inspection and functional testing | Vision systems, leak testers, force testers | Very High (30-50 sensors) |
| S6: Packaging | Primary and secondary packaging, labeling | Pouch sealers, cartoners, labelers, case packers | Medium (15-25 sensors) |
| S7: Palletizing/Shipping | Tertiary packaging, palletizing, shipping prep | Palletizers, stretch wrappers, labeling | Low (8-12 sensors) |

# 4. Programmable Logic Controller (PLC) Configuration

## 4.1 PLC Strategy & Vendor Recommendation

The PLC strategy follows a standardized-platform approach with a single primary vendor ecosystem to minimize integration complexity, spare parts inventory, and training requirements while maintaining the flexibility to integrate specialized controllers where process-specific requirements demand it.

### 4.1.1 Primary PLC Platform: Rockwell Automation Allen-Bradley

Recommendation: Rockwell Automation ControlLogix 5580 family as the primary PLC platform, with CompactLogix 5380 for smaller stations and GuardLogix for safety-rated applications.

Rationale for Rockwell selection in a Hollister context:

- Market-leading installed base in North American and European medical device manufacturing

- Integrated safety (GuardLogix) eliminates separate safety controller hardware for most applications

- Native EtherNet/IP with CIP (Common Industrial Protocol) provides unified communications

- FactoryTalk suite provides SCADA/historian/analytics within a single ecosystem

- Strong regulatory validation support with established 21 CFR Part 11 compliance templates

- Global service network including Ireland-based field engineering

### 4.1.2 Secondary PLC Platform: Siemens (Interoperability Layer)

Siemens S7-1500 series is recommended as a secondary platform for specific use cases: legacy integration where Siemens PLCs are already deployed, specialized motion control applications where Siemens SIMOTION excels, and interoperability validation to ensure the architecture is not single-vendor dependent.

## 4.2 PLC Allocation per Manufacturing Line

Each manufacturing line requires a carefully balanced allocation of PLCs that balances granularity of control against complexity of integration. The following allocation is recommended per baseline manufacturing line:

| Station | Primary PLC | Qty | Safety PLC | Qty | I/O Points (est.) | Justification |
| --- | --- | --- | --- | --- | --- | --- |
| S1: Raw Material Prep | CompactLogix 5380 | 1 | Compact GuardLogix | 1 | 64-96 | Lower complexity; compact form factor sufficient |
| S2: Forming/Molding | ControlLogix 5580 | 2 | GuardLogix 5580 | 1 | 192-256 | High I/O density; critical process control; redundant pair recommended |
| S3: Assembly | ControlLogix 5580 | 1 | GuardLogix 5580 | 1 | 128-192 | Complex motion coordination; integrated safety zones |
| S4: Coating/Treatment | ControlLogix 5580 | 1 | Compact GuardLogix | 1 | 96-160 | Precision process control; thermal management |
| S5: Inspection/Testing | CompactLogix 5380 | 2 | N/A (non-safety) | 0 | 64-128 | Vision system coordination; parallel test stations |
| S6: Packaging | ControlLogix 5580 | 1 | GuardLogix 5580 | 1 | 128-192 | High-speed coordination; serialization/track-and-trace |
| S7: Palletizing | CompactLogix 5380 | 1 | Compact GuardLogix | 1 | 48-64 | Robotic coordination; lower complexity |
| Line Coordinator | ControlLogix 5580 | 1 | N/A | 0 | 32-48 | Line-level orchestration; recipe management; MES interface |

Total per Manufacturing Line: 10 primary PLCs + 6 safety PLCs = 16 controllers. Estimated total I/O: 752-1,136 points.

## 4.3 PLC Configuration per Plant (Full Deployment)

Scaling the per-line allocation to a full plant with 6-8 manufacturing lines:

| Component | Per Line | 6 Lines | 8 Lines | Plant Infrastructure | Plant Total (8 Lines) |
| --- | --- | --- | --- | --- | --- |
| ControlLogix 5580 | 6 | 36 | 48 | 4 (utilities, BMS, WH) | 52 |
| CompactLogix 5380 | 4 | 24 | 32 | 6 (aux systems) | 38 |
| GuardLogix 5580 | 3 | 18 | 24 | 2 (plant safety) | 26 |
| Compact GuardLogix | 3 | 18 | 24 | 2 (plant safety) | 26 |
| Total Controllers | 16 | 96 | 128 | 14 | 142 |
| Est. I/O Points | ~950 | ~5,700 | ~7,600 | ~1,200 | ~8,800 |

## 4.4 PLC Network Architecture

All PLCs communicate via EtherNet/IP on a segmented, ring-topology industrial Ethernet network. Each manufacturing line operates on its own VLAN with a managed switch stack. The network design follows:

- Device Level Ring (DLR): EtherNet/IP ring topology per station for sub-millisecond failover

- Line Level Backbone: Managed Stratix 5700 switches per line with inter-line trunking

- Plant Backbone: Stratix 5400 Layer 3 switches for routing between line VLANs and plant DMZ

- Redundancy: All critical PLCs deployed in 1oo2 (one-out-of-two) redundant pairs for forming/molding stations

- Time Synchronization: IEEE 1588 Precision Time Protocol (PTP) for sub-microsecond synchronization across all PLCs

## 4.5 PLC Programming Standards

All PLC programs shall adhere to IEC 61131-3 with the following Hollister-specific standards:

- Structured Text (ST) as the primary language for complex logic and calculations

- Function Block Diagram (FBD) for regulatory logic and interlocks

- Sequential Function Charts (SFC) for batch/recipe control aligned with ISA-88

- Ladder Logic (LD) reserved only for discrete I/O interlocking where required by maintenance familiarity

- All programs version-controlled in a validated source control system (e.g., Rockwell AssetCentre or AVEVA Teamwork)

- Add-On Instructions (AOIs) library for standardized functions reusable across all plants

# 5. Distributed Control System (DCS) Configuration

## 5.1 DCS Strategy

For Hollister's medical device manufacturing, the architecture recommends a hybrid DCS/PLC approach rather than a pure DCS deployment. This reflects the discrete manufacturing nature of Hollister's products (as opposed to continuous process industries) while providing the supervisory coordination, batch management, and regulatory data management capabilities that a DCS excels at.

### 5.1.1 Recommended Platform: Rockwell PlantPAx

Primary Recommendation: Rockwell PlantPAx 5.0 as the DCS layer, providing a seamless integration with the ControlLogix PLC infrastructure. PlantPAx is implemented as a distributed control architecture on top of the existing PLC hardware, eliminating the need for separate DCS hardware while providing full DCS functionality.

Alternative (for consideration): Emerson DeltaV or Siemens PCS 7 if the organization requires a traditional DCS with independent hardware. This would add cost and integration complexity but provides vendor diversity for critical processes.

## 5.2 DCS Scope per Manufacturing Line

The DCS layer provides the following functions per manufacturing line:

| DCS Function | Implementation | Components | Qualification |
| --- | --- | --- | --- |
| Supervisory Control | PlantPAx process objects running on Line Coordinator PLC | Recipe manager, sequence coordinator, material tracker | IQ/OQ/PQ per ISA-88 |
| Batch Management | ISA-88 compliant batch engine | Recipe phases, unit procedures, master recipes | GAMP 5 Cat 4/5 |
| Operator Interface | FactoryTalk View SE distributed HMI | 3x operator stations per line, 1x supervisor station | 21 CFR Part 11 validated |
| Historian | FactoryTalk Historian SE | Continuous data at 1-second resolution; event-driven for alarms | Validated, Part 11 compliant |
| Alarm Management | PlantPAx alarm strategy per ISA-18.2 | Alarm rationalization, shelving, suppression audit trail | IQ/OQ required |
| Report Generation | FactoryTalk VantagePoint + SSRS | Batch reports, OEE, quality metrics, environmental logs | Validated output |

## 5.3 DCS Architecture per Plant

At the plant level, the DCS provides coordination across all manufacturing lines plus shared utilities:

- Plant-Wide Historian: Consolidated data from all lines with 5+ year retention for trend analysis and regulatory queries

- Centralized Alarm Console: Aggregated alarm view for plant operations center, conforming to EEMUA 191

- Utility Systems Integration: BMS (HVAC, clean room), purified water systems, compressed air, electrical distribution

- Environmental Monitoring System (EMS): Integrated particle counters, differential pressure, temperature, humidity across all clean rooms

- MES Gateway: OPC-UA server providing standardized data access for Level 3 systems

## 5.4 DCS Redundancy & High Availability

The DCS layer is configured for high availability with the following redundancy model:

- Server Redundancy: Hot standby for all PlantPAx servers (application, historian, HMI) with automatic failover < 10 seconds

- Network Redundancy: Dual-homed Ethernet connections with RSTP for all DCS nodes

- Historian Redundancy: Primary + mirror historian with store-and-forward buffering at each data source

- Operator Station Redundancy: Any operator station can control any line (role-based, not hardware-based)

- UPS Protection: All DCS components on dedicated UPS with minimum 30-minute runtime plus generator backup

# 6. Comprehensive Sensor Architecture

## 6.1 Sensor Strategy Overview

The sensor architecture is organized into three categories: vendor-specific sensors that are tied to particular equipment, common sensors deployed uniformly across all plants, and facility-level sensors for building and environmental management. All sensors are selected for Industry 4.0 readiness with native digital communication (IO-Link, EtherNet/IP, HART, or PROFINET) to enable direct data access without analog signal degradation.

## 6.2 Manufacturing Equipment Sensors (Vendor-Specific)

These sensors are selected based on specific machine types and process requirements. The following represents the recommended sensor suite per station type:

### 6.2.1 Station S2: Forming/Molding — Highest Sensor Density

| Measurement | Sensor Type | Recommended Vendor/Model | Qty per Station | Protocol | Accuracy |
| --- | --- | --- | --- | --- | --- |
| Mold Temperature | RTD (Pt100) multi-zone | Endress+Hauser iTEMP TMT72 | 8-12 | HART/IO-Link | ±0.1°C |
| Injection Pressure | Piezoelectric cavity pressure | Kistler 6183C | 4-6 | ComoNeo analog + digital | ±0.5% FS |
| Clamping Force | Strain gauge load cell | HBM C9B | 2-4 | Analog/amplifier | ±0.02% FS |
| Cycle Time | Inductive proximity | Balluff BES M18 | 4-6 | IO-Link | ±0.1 ms |
| Material Flow | Coriolis mass flow | Endress+Hauser Promass F300 | 1-2 | EtherNet/IP | ±0.1% |
| Barrel Temperature | Thermocouple Type J/K | WatlowDERA | 4-8 | HART | ±1.5°C |
| Hydraulic Pressure | Pressure transmitter | WIKA S-20 | 4-6 | IO-Link | ±0.25% FS |
| Part Presence | Photoelectric | SICK W16 | 6-8 | IO-Link | N/A (discrete) |
| Part Dimensions (In-line) | Laser micrometer | Keyence LS-9030 | 2-4 | EtherNet/IP | ±1 μm |

### 6.2.2 Station S5: Inspection/Testing — Highest Precision

| Measurement | Sensor Type | Recommended Vendor/Model | Qty per Station | Protocol | Accuracy |
| --- | --- | --- | --- | --- | --- |
| Visual Inspection | Machine vision camera | Cognex In-Sight 9912 | 4-8 | GigE Vision/EtherNet/IP | Sub-pixel |
| Surface Defect | 3D line scan profiler | Keyence LJ-X8000 | 2-4 | EtherNet/IP | ±0.5 μm Z |
| Leak Testing | Pressure decay tester | ATEQ F620 | 2-4 | Serial/EtherNet | ±0.01 mbar |
| Force/Peel Testing | Load cell with linear actuator | Mark-10 M5-100 | 2-4 | USB/Serial | ±0.1% FS |
| Dimensional (CMM proxy) | Laser triangulation | Micro-Epsilon scanCONTROL | 1-2 | EtherNet/IP | ±2 μm |
| Color/Appearance | Spectrophotometer inline | X-Rite Ci7860 | 1-2 | Serial/Ethernet | ΔE*<0.04 |
| Weight Check | Precision checkweigher | Mettler Toledo XS | 1-2 | EtherNet/IP | ±0.01 g |
| Barcode/2D Code | Vision reader | Cognex DataMan 475V | 2-4 | EtherNet/IP | 99.9% read rate |

## 6.3 Common Sensors (Standardized Across All Plants)

The following sensors are deployed identically across every plant and manufacturing line, enabling cross-plant comparisons, unified analytics, and simplified spare parts management.

### 6.3.1 Environmental Monitoring (Clean Room & Controlled Areas)

| Measurement | Sensor | Vendor/Model | Deployment | Protocol |
| --- | --- | --- | --- | --- |
| Particle Count (0.5-5 μm) | Optical particle counter | TSI AeroTrak 9310 | 1 per clean room zone + critical points | Modbus TCP/MQTT |
| Temperature | RTD (Pt100) with transmitter | Vaisala TMW110 | Grid: 1 per 50 m² in clean rooms | Modbus TCP |
| Relative Humidity | Capacitive humidity/temp | Vaisala HMT330 | Grid: 1 per 100 m² | Modbus TCP |
| Differential Pressure | Low-range DP transmitter | Setra Model 267 | Every room/corridor boundary | BACnet/Modbus |
| Airflow Velocity | Thermal anemometer | TSI VelociCalc 9565 | LAF hoods, critical air returns | Analog/logged |
| CO2 / VOC | NDIR CO2 + PID VOC | Honeywell AQ110 series | Occupied areas, solvent zones | BACnet |

### 6.3.2 Utility Monitoring

| Utility | Measurements | Sensor Vendor/Model | Deployment |
| --- | --- | --- | --- |
| Compressed Air | Pressure, flow, dew point, oil content | BEKO METPOINT series (OCV, DPM, FLM) | Main header + each line drop |
| Purified Water (WFI/PW) | Conductivity, TOC, temperature, flow | Endress+Hauser Liquiline CM442 + Memosens | Generation, storage, each use point |
| Electrical Power | V, I, kW, kWh, PF, harmonics | Schneider PowerLogic PM8000 | Main switchgear + each MCC/panel |
| HVAC/AHU | Supply/return temp, filter DP, damper pos | Siemens Desigo CC sensors | Each AHU serving clean rooms |
| Steam/Hot Water | Pressure, temperature, flow | Endress+Hauser Prowirl F200 + TMT82 | Boiler headers, sterilization points |
| Nitrogen/Specialty Gas | Pressure, purity (O2 content), flow | Hamilton VisiFerm (purity) + E+H flow | Generation/storage + use points |

### 6.3.3 Machine Health / Predictive Maintenance

| Measurement | Sensor | Vendor/Model | Deployment |
| --- | --- | --- | --- |
| Vibration (tri-axial) | MEMS accelerometer + ICP piezo | Fluke 3561 FC (wireless) + PCB 356A45 (wired) | Every rotating machine >5 kW |
| Motor Current Signature | Current transformer + analyzer | Schneider PowerLogic ION9000 | Critical motors on forming/packaging |
| Bearing Temperature | RTD skin sensor | ifm TN2531 (IO-Link) | Critical bearing housings |
| Oil Condition | Dielectric / moisture / particle | HYDAC Lab CM-A5/2 | Hydraulic systems on presses |
| Ultrasonic Leak Detection | Airborne ultrasonic | SDT 340 (portable + fixed) | Compressed air leaks, steam traps |

## 6.4 Camera Systems

Camera deployments serve three distinct purposes: machine vision (quality), process monitoring, and facility security. Each has different specifications and governance requirements.

### 6.4.1 Machine Vision Cameras (Quality / Inspection)

Covered under Station S5 above. These are high-resolution, precisely calibrated cameras treated as metrology instruments with full IQ/OQ/PQ qualification. Recommended: Cognex In-Sight 9000 series and Keyence CV-X400 series.

### 6.4.2 Process Monitoring Cameras

| Application | Camera Type | Vendor/Model | Resolution | Deployment |
| --- | --- | --- | --- | --- |
| Operator Activity (ergonomics/safety) | Fixed IP camera with analytics | Axis P3267-LVE with ACAP | 5 MP | 2 per station (overhead + side) |
| Material Flow Tracking | Fixed wide-angle | Axis M3068-P (fisheye) | 12 MP | Corridor intersections, staging areas |
| Changeover Verification | PTZ with preset tours | Axis Q6135-LE | 1080p/60fps | 1 per line (critical changeover area) |
| Thermal Monitoring | Thermal overlay | FLIR A500/A700 | 640x480 thermal | Electrical panels, high-heat processes |

### 6.4.3 Facility Security Cameras

| Zone | Camera Type | Vendor/Model | Deployment Density |
| --- | --- | --- | --- |
| Perimeter / Parking | 4K bullet with IR | Axis Q1808-LE | Per security assessment (typically 1/25m perimeter) |
| Building Entrances | Dome with face detection | Axis P3268-LVE | Every entrance/exit + loading docks |
| Corridors / Warehouse | Panoramic 360° | Axis M4328-P | 1 per 200 m² open area |
| Clean Room Entrances | Compact dome | Axis M3116-LVE | Every gowning room entry/exit |
| Server Room / MDF | Fixed with analytics | Axis P3265-LVE | 2 per room (entry + equipment view) |

Camera Platform Standard: Axis Communications is recommended as the standard camera vendor across all plants for consistency in management (AXIS Camera Station Pro), analytics ecosystem (ACAP), and cybersecurity features (Axis Edge Vault, signed firmware). Video management integrates to plant security operations center and optionally to AI-based analytics in the edge/cloud compute layer.

# 7. Human Activity Monitoring

## 7.1 Scope & Ethical Framework

Human activity monitoring in a cGMP medical device facility serves three purposes: worker safety, compliance documentation (operator actions as part of batch records), and process optimization. All monitoring must comply with GDPR (given the Ireland baseline), local labor laws, and Hollister's corporate ethics policies. No biometric surveillance or individual performance scoring is implemented without explicit works council/employee representative agreement.

## 7.2 Monitoring Technologies

| Capability | Technology | Vendor/Solution | Data Governance |
| --- | --- | --- | --- |
| Badge-Based Access | RFID/NFC proximity readers | HID iCLASS SE + Lenel OnGuard | 21 CFR Part 11 e-signature; personnel ID tied to batch records |
| Operator Position Tracking | UWB real-time location (RTLS) | Sewio UWB RTLS | Zone-level granularity only; no individual path tracking stored >24h |
| Gowning Compliance | AI vision analytics | Axis ACAP + custom ML model | Alert-only; no video recording of individuals; aggregate compliance metrics |
| Ergonomic Assessment | Wearable IMU sensors (voluntary) | Kinetic Reflex system | Opt-in only; anonymized aggregate data to EHS; individual data deleted <7 days |
| Operator Actions (Batch Record) | Electronic batch record (EBR) interaction | MES system (e.g., MasterControl) | Full 21 CFR Part 11 audit trail; permanent retention per batch |
| Training Verification | LMS integration + badge scan | ComplianceWire / Veeva Vault QMS | Training records integrated with operator authorization for equipment |

# 8. IoT, Compute, Storage & Network Infrastructure

## 8.1 IoT Gateway Architecture

IoT gateways bridge the gap between field-level sensors (Level 0-1) and the IT/OT convergence layer (Level 3-3.5). The gateway strategy follows a tiered approach:

| Tier | Gateway | Vendor/Model | Deployment | Function |
| --- | --- | --- | --- | --- |
| Tier 1: Station | Compact edge gateway | Advantech UNO-2484G or Moxa UC-8200 | 1 per station (7 per line) | Protocol conversion (IO-Link, Modbus, HART to OPC-UA/MQTT); local buffering |
| Tier 2: Line | Edge compute gateway | Dell Edge Gateway 5200 or HPE EL300 | 1 per manufacturing line | Data aggregation, local analytics, ML inference, historian buffering |
| Tier 3: Plant | Edge server cluster | See Section 8.2 On-Premise Compute | 1 per plant (in server room) | Plant historian, MES, SCADA servers, virtual PLC, AI/ML training |

## 8.2 On-Premise Compute Infrastructure

Given the regulatory requirements for data sovereignty, low-latency control, and operational autonomy during WAN outages, the primary compute infrastructure is on-premise with selective cloud extension.

### 8.2.1 Server Room Configuration (per Plant)

| Function | Hardware | Qty | Specifications | Redundancy |
| --- | --- | --- | --- | --- |
| Virtualization Hosts | Dell PowerEdge R760 | 4 | 2x Xeon Gold 6430, 512GB RAM, 2x 1.6TB NVMe | VMware vSphere HA cluster (N+1) |
| Historian/Database | Dell PowerEdge R760 | 2 | 2x Xeon Gold 6430, 1TB RAM, 8x 3.84TB SSD RAID10 | Active-passive replication |
| Edge AI/ML Inference | Dell PowerEdge R760xa | 2 | 2x Xeon + 2x NVIDIA L40S GPU, 512GB RAM | Active-active load balanced |
| Backup/DR | Dell PowerEdge R660 | 2 | 1x Xeon Silver 4416+, 256GB RAM, 24x 12TB HDD | Veeam replication to secondary site |
| SAN Storage | Dell PowerStore 1200T | 1 | 50TB usable all-flash, 100GbE NVMe-oF | Dual controller active-active |
| Network Core | Cisco Catalyst 9500 stack | 2 | 48x 10GbE + 8x 100GbE uplinks | VSS/StackWise Virtual pair |

### 8.2.2 Cloud Extension (Off-Site Compute)

Cloud services supplement on-premise capabilities for non-real-time functions:

| Function | Cloud Provider | Service | Data Classification |
| --- | --- | --- | --- |
| Enterprise Data Lake | Microsoft Azure | Azure Data Lake Storage Gen2 + Databricks | Anonymized process data; no PII/PHI |
| Advanced Analytics / AI Training | Microsoft Azure | Azure Machine Learning + GPU Compute | Aggregated production data; no batch-identifiable data |
| Digital Twin (Enterprise) | Microsoft Azure | Azure Digital Twins + IoT Hub | Plant/line models; validated simulation data |
| Disaster Recovery | Microsoft Azure | Azure Site Recovery + Blob Storage | Encrypted replicas; geo-redundant |
| Supply Chain Integration | AWS or Azure | API Gateway + Integration Platform | EDI, ASN, PO data; encrypted in transit/rest |

Cloud Selection Rationale: Microsoft Azure is recommended as the primary cloud platform due to its strong life sciences validation support (GxP qualification for Azure), native integration with Microsoft enterprise tools (Active Directory, Power BI), and EU data residency options (Ireland Azure region for GDPR compliance). AWS serves as secondary for supply chain integration where trading partners require it.

## 8.3 Network Architecture

### 8.3.1 Network Segmentation (ISA-95 Aligned)

| Network Zone | VLAN Range | Switch Platform | Firewall/DMZ | Purpose |
| --- | --- | --- | --- | --- |
| Level 0-1: Field | VLAN 100-199 | Stratix 5700 (managed) | None (air-gapped from IT) | PLCs, sensors, actuators, I/O |
| Level 2: Control | VLAN 200-299 | Stratix 5400 (L3) | OT Firewall (Palo Alto OT) | DCS, SCADA, historian, HMI |
| Level 3: MES/MOM | VLAN 300-399 | Cisco Catalyst 9300 | OT/IT Firewall | MES, QMS, batch records, scheduling |
| Level 3.5: DMZ | VLAN 350 | Cisco Catalyst 9500 | Dual firewall (OT + IT) | OPC-UA aggregation, data diode, protocol break |
| Level 4: Enterprise | VLAN 400-499 | Cisco Catalyst 9500 | IT Firewall + WAF | ERP, PLM, email, business apps |
| Level 5: Cloud/WAN | N/A | Cisco SD-WAN (Viptela) | Next-gen firewall + CASB | Cloud services, inter-site connectivity |
| Guest/IoT | VLAN 900-999 | Cisco Catalyst 9300 | Isolated; NAC-controlled | Visitor Wi-Fi, non-critical IoT |

### 8.3.2 Network Bandwidth & Redundancy

- Field to Station Gateway: 100 Mbps Ethernet (DLR ring topology) per device cluster

- Station to Line Gateway: 1 Gbps Ethernet (redundant paths) per station

- Line to Plant Core: 10 Gbps fiber uplinks (dual-homed) per line switch stack

- Plant Core to DMZ/Enterprise: 100 Gbps fiber backbone (redundant)

- Plant to Cloud/WAN: Dual ISP with SD-WAN; 1 Gbps primary, 500 Mbps secondary; encrypted overlay

- Wireless (where needed): Wi-Fi 6E (Cisco Catalyst 9164) for mobile devices; private 5G evaluation for future AGV/AMR

# 9. Metrology, Calibration & Measurement Assurance

## 9.1 Metrology Strategy

Every measurement device in the digital footprint—from a simple temperature sensor to a coordinate measuring machine—is subject to a calibration management regime traceable to national/international standards (NIST, NPL, PTB). The metrology system is integral to the cGMP compliance framework and directly supports the IQ/OQ/PQ qualification process.

## 9.2 Calibration Management System

Recommended Platform: Blue Mountain Regulatory Asset Manager (RAM) or Beamex CMX, integrated with the MES/QMS for automated calibration scheduling, out-of-tolerance alerting, and impact assessment on batch records.

| Calibration Tier | Scope | Frequency | Standard | Performer |
| --- | --- | --- | --- | --- |
| Tier 1: Reference Standards | Plant reference instruments | Annual (accredited lab) | ISO 17025 accredited cal lab | External (e.g., Trescal, Endress+Hauser) |
| Tier 2: Working Standards | Metrology lab instruments | Semi-annual | Traceable to Tier 1 | In-house metrology team |
| Tier 3: Production Instruments | In-line sensors, transmitters | Per SOP (risk-based: 3-12 months) | Traceable to Tier 2 | Calibration technicians |
| Tier 4: Automated/Self-Calibrating | Smart sensors with self-diagnostics | Continuous (verification) + periodic full cal | IO-Link/HART self-diagnostics | Automated with human verification |

## 9.3 Measurement Assurance Program

- Statistical Process Control (SPC): All critical measurements monitored with automated SPC charting and out-of-control alerts

- Gauge R&R: Required for all new measurement systems per AIAG MSA 4th Edition or equivalent

- Measurement Uncertainty Budgets: Established for every critical-to-quality (CTQ) measurement per GUM (Guide to the Expression of Uncertainty in Measurement)

- Out-of-Tolerance (OOT) Impact Assessment: Automated batch impact analysis when a calibration fails, identifying all batches produced since last known good calibration

- Digital Calibration Certificates: All calibration data stored electronically with 21 CFR Part 11 compliant electronic signatures

# 10. Qualification Framework: IQ/OQ/PQ & V&V

## 10.1 Qualification Strategy

The qualification framework ensures every component of the digital footprint is installed, operates, and performs as intended under cGMP conditions. The approach follows GAMP 5 (Second Edition) and aligns with ISPE Commissioning and Qualification Baseline Guide.

## 10.2 Qualification Scope per Component Category

| Component Category | GAMP Cat. | IQ Scope | OQ Scope | PQ Scope |
| --- | --- | --- | --- | --- |
| Sensors/Transmitters | Cat 1 (Std HW) | Installation per spec, wiring, calibration verification | Signal accuracy, response time, alarm functions | Performance over 3 production batches; drift analysis |
| PLCs | Cat 3-4 | Hardware install, firmware version, I/O wiring, network config | Logic execution, safety functions, failover, alarm response | Full production scenario including abnormal conditions |
| DCS/SCADA | Cat 4-5 | Server install, software version, network connectivity | All control functions, alarms, historian data integrity, Part 11 | 3 consecutive production days; operator workflow validation |
| MES | Cat 5 (Custom) | Server/client install, database config, interfaces | All business rules, electronic batch record, deviation handling | End-to-end batch processing with intentional deviations |
| IoT Gateways | Cat 3 | Installation, network config, protocol config | Data throughput, latency, store-and-forward, failover | Performance under peak load for sustained production |
| Network Infrastructure | Cat 1-3 | Switch/firewall install, VLAN config, cabling certification | Throughput, latency, failover, segmentation validation | Traffic under production load; failover timing |
| Compute/Storage | Cat 1-3 | Hardware install, OS/hypervisor, storage provisioning | Performance, redundancy, backup/restore, access control | Sustained load testing; disaster recovery exercise |
| Cameras (Quality) | Cat 3-4 | Mounting, alignment, lighting, calibration | Detection accuracy, repeatability, lighting sensitivity | Known defect challenge kit; false positive/negative rates |
| Environmental Monitoring | Cat 3 | Sensor placement per mapping study, calibration | Alarm thresholds, data recording, excursion handling | Environmental challenge testing; worst-case scenarios |

## 10.3 V&V for Systems Engineering

The end-to-end Verification and Validation (V&V) process follows the V-Model, ensuring traceability from user requirements through to operational performance:

- User Requirements Specification (URS): Business and regulatory requirements defining what the system must do

- Functional Requirements Specification (FRS): How the system will fulfill each URS requirement

- Design Specification (DS): Detailed technical design including hardware, software, and configuration specifications

- Factory Acceptance Testing (FAT): Verification at vendor site before shipment (where applicable)

- Site Acceptance Testing (SAT): Verification of installation and basic function at the Hollister facility

- Installation Qualification (IQ): Documented verification that equipment is installed per approved specifications

- Operational Qualification (OQ): Documented verification that equipment operates per approved specifications across operating ranges

- Performance Qualification (PQ): Documented verification that the system consistently performs as intended under actual production conditions

Traceability Matrix: A requirements traceability matrix (RTM) links every URS requirement through FRS, DS, and test protocols to test results, ensuring complete V&V coverage with no gaps.

# 11. Manufacturing on Demand (MOD) Accommodations

## 11.1 MOD Architecture Requirements

Manufacturing on Demand requires the digital footprint to support rapid product changeover, dynamic batch sizing, configurable process parameters, and real-time demand signal integration. The architecture accommodates MOD through the following mechanisms:

## 11.2 Recipe-Driven Production

- ISA-88 Recipe Model: All production parameters encoded in hierarchical recipes (master recipe, control recipe, equipment recipe) managed within the DCS batch engine

- Dynamic Recipe Selection: MES-driven recipe download to PLCs based on production schedule, allowing automated changeover between products on the same line

- Parameter Sets: Modular parameter groups that can be mixed and matched for new product variants without new PLC programming

- Golden Batch Profiling: Statistical reference profiles for each product, enabling real-time deviation detection during production

## 11.3 Rapid Changeover Support

- Digital Work Instructions: Augmented reality (AR) or tablet-based changeover guides with visual verification steps, integrated with the MES

- Changeover Verification: Automated sensor-based verification that changeover steps are complete (e.g., vision confirmation of tooling, sensor confirmation of cleaning completion)

- Changeover Time Tracking: Automated SMED (Single Minute Exchange of Die) metrics with OEE integration

- Pre-Staged Recipes: Predictive recipe staging based on production schedule, pre-loading next product parameters during current run

## 11.4 Dynamic Resource Allocation

- Flexible Line Assignment: Production scheduling system allocates products to lines based on capability, availability, and efficiency optimization

- Shared Equipment Pool: Inspection stations and packaging lines configurable for multiple product families through recipe-driven setup

- Material Kanban: IoT-enabled material replenishment triggered by real-time consumption data from line sensors

- Labor Allocation: Operator skill matrix integrated with MES for dynamic assignment of qualified personnel to production activities

# 12. Interim PLM Solution

## 12.1 Interim PLM Strategy

Hollister requires immediate product lifecycle management capabilities but is not yet ready to commit to a permanent enterprise PLM platform. The interim solution must provide essential PLM functions while maintaining clean data models and migration paths that will support any future PLM selection.

Guiding Principle: The interim PLM serves as a structured data container and workflow engine, not as a permanent system of record. All data structures follow open standards (STEP AP242, PLM XML, or equivalent) to ensure vendor-agnostic extractability.

## 12.2 Interim PLM Platform Recommendation

### 12.2.1 Primary Recommendation: Aras Innovator (Open Source Core)

Aras Innovator is recommended as the interim PLM for the following reasons:

- Open-source core with no per-seat licensing, reducing commitment risk

- Resilient, enterprise-grade platform used by major manufacturers (Airbus, Motorola)

- Open data model using SQL Server with well-documented schema, enabling straightforward data extraction/migration

- Built-in configuration management, change control, and document management meeting cGMP requirements

- REST API and web services for integration with MES, ERP, and engineering tools

- Supports FDA 21 CFR Part 11 with electronic signatures and audit trails

### 12.2.2 Alternative: SharePoint-Based PLM Lite (Lower Capability)

If the organization prefers to leverage existing Microsoft infrastructure, a structured SharePoint Online deployment with Power Automate workflows can provide basic PLM functions: document control, change request workflows, BOM management via linked lists. This option is lower-capability but has near-zero incremental cost and familiar user interface. The risk is data structure limitations that may complicate future migration.

## 12.3 Interim PLM Functional Scope

| PLM Function | Interim Implementation | Migration Readiness |
| --- | --- | --- |
| Bill of Materials (BOM) | Aras BOM management with part-item-BOM hierarchy | Export to STEP AP242 or CSV; standard BOM structure |
| Document Control | Aras document management with revision control, approval workflows | File-based extraction with metadata; standard naming conventions |
| Change Management | ECR/ECO/ECN workflow in Aras with impact analysis | Change history exported as structured data with full audit trail |
| Configuration Management | Product effectivity, serialization rules, variant management | Configuration baseline snapshots exportable to any PLM |
| CAD Data Management | Aras vault with CAD connector (SolidWorks, CATIA, AutoCAD) | CAD files + metadata export; neutral format (STEP, JT) mandatory |
| Supplier Collaboration | Aras Secure Social with supplier portal for drawing markup | Supplier data in standard format; independent of PLM platform |
| R&D to Mfg Tech Transfer | Stage-gate workflow with design transfer checklist | Transfer package as structured data package; process-independent |
| Regulatory Submission Support | Document linking, DHF/DMR/DHR organization | Regulatory dossier structure exportable as XML/PDF package |

## 12.4 PLM-MES Integration (Critical Interface)

The interim PLM must feed validated production specifications to the MES/DCS layer. This interface is critical for cGMP compliance and is designed to be PLM-vendor-agnostic:

- Integration Bus: Apache Kafka or Azure Service Bus as the middleware, with standardized B2MML (ISA-95 XML) message formats

- Master Data: Product definitions, BOM, process specifications published from PLM to a shared Master Data Management (MDM) layer

- Recipe Translation: PLM process specifications translated to ISA-88 recipes through a Recipe Management Service, decoupled from both PLM and DCS

- Change Propagation: ECO approval in PLM triggers change notification to MES, which manages the manufacturing-side impact assessment and implementation

Critical Design Decision: The Recipe Management Service is an independent microservice that sits between PLM and DCS. When the permanent PLM is selected, only the PLM-to-RMS interface changes; the RMS-to-DCS interface and all validated recipes remain untouched.

# 13. Technology Transfer & Change Control

## 13.1 R&D to Manufacturing Tech Transfer

The technology transfer process is the highest-risk interface in the product lifecycle for a medical device manufacturer. The digital footprint supports smooth handoffs through:

### 13.1.1 Design Transfer Package (Digital)

- Digital Design History File (DHF): Complete product development documentation managed in interim PLM, including design inputs, outputs, verification, and validation records

- Process Design Package: Manufacturing process specifications, equipment requirements, critical process parameters (CPPs), and critical quality attributes (CQAs) encoded in structured data formats

- Recipe Template: Pre-validated ISA-88 recipe structure with parameterized CPPs, ready for site-specific equipment mapping

- Measurement System Specification: Required measurement capabilities, accuracy requirements, and gauge R&R acceptance criteria for every CTQ measurement

- Validation Master Plan Template: Pre-defined IQ/OQ/PQ protocol templates populated with product-specific acceptance criteria from design transfer

### 13.1.2 Digital Thread Continuity

The architecture maintains a digital thread from R&D design intent through manufacturing execution:

- Requirements Traceability: URS/FRS requirements link through design specifications to manufacturing parameters to test results

- Process Analytical Technology (PAT): Real-time process monitoring parameters defined during R&D validated as in-process controls during manufacturing

- Knowledge Management: Lessons learned, process development reports, and deviation histories captured in structured knowledge base accessible to manufacturing engineering

## 13.2 Change Control Framework

Change control is the governance mechanism ensuring every modification to the validated state is assessed, approved, implemented, and verified. The digital footprint implements a multi-tier change control system:

| Change Tier | Scope | Approval | V&V Required | Example |
| --- | --- | --- | --- | --- |
| Tier 1: Critical | Change to validated system affecting product quality or patient safety | QA Director + Engineering Director + Regulatory | Full re-qualification (IQ/OQ/PQ) | PLC program change affecting process control; new sensor type |
| Tier 2: Major | Change to validated system with indirect quality impact | QA Manager + Engineering Manager | Partial re-qualification (OQ/PQ typically) | Firmware update; network reconfiguration; HMI screen change |
| Tier 3: Minor | Change to non-validated system or like-for-like replacement | Engineering Manager | Verification testing only | Like-for-like sensor replacement; switch replacement |
| Tier 4: Emergency | Unplanned change required for production continuity | Shift Supervisor (retroactive full approval within 48h) | Post-implementation qualification | Emergency PLC patch; failed sensor replacement |

## 13.3 Configuration Management

All system configurations are managed as configuration items (CIs) in a Configuration Management Database (CMDB):

- PLC Programs: Stored in version-controlled repository (Rockwell AssetCentre) with change history, approval records, and rollback capability

- DCS Configuration: Server images, historian configuration, alarm setpoint databases versioned and backed up with automated comparison tools

- Network Configuration: Firewall rules, VLAN assignments, switch configs managed via Cisco DNA Center with change approval integration

- Sensor Configuration: IO-Link parameter sets, HART configuration data backed up to centralized repository

- Server/VM Configuration: Infrastructure-as-Code (Ansible/Terraform) for reproducible server builds; golden images maintained for rapid recovery

- Firmware Registry: Approved firmware versions for every device category maintained in CMDB; firmware updates require change control approval

# 14. cGMP Compliance Architecture

## 14.1 Regulatory Mapping

The digital footprint is designed with compliance as an inherent property, not an afterthought. The following table maps key regulatory requirements to architectural features:

| Regulation | Key Requirements | Architecture Implementation |
| --- | --- | --- |
| FDA 21 CFR Part 11 | Electronic records, electronic signatures, audit trails | All systems Level 2+ configured with Part 11 controls: e-signatures, audit trails, access control, system validation |
| FDA 21 CFR 211 | cGMP for finished pharmaceuticals (referenced for devices) | Environmental monitoring, calibration management, batch records, deviation handling, CAPA integration |
| FDA 21 CFR 820 | Quality System Regulation for devices | Design controls (DHF in PLM), production controls (MES), CAPA, complaint handling, document control |
| EU MDR 2017/745 | Medical Device Regulation (EU) | UDI integration, post-market surveillance data collection, technical documentation management in PLM |
| ISO 13485:2016 | Quality management systems for medical devices | Process validation (IQ/OQ/PQ), risk management (ISO 14971 integration), measurement management (ISO 10012) |
| GAMP 5 (2nd Ed.) | Good Automated Manufacturing Practice | Risk-based approach to computerized system validation; categorization of all systems; validation lifecycle documentation |
| IEC 62443 | Industrial cybersecurity | Zone/conduit model, security levels per zone, patch management, access control, incident response |
| GDPR | Data protection (EU/Ireland) | Human activity data minimization, consent management, data retention limits, right to erasure compliance |

## 14.2 Data Integrity (ALCOA+ Principles)

All electronic data generated by the digital footprint adheres to ALCOA+ principles:

- Attributable: Every data entry linked to the person or system that generated it (Part 11 user ID, system ID)

- Legible: Data presented in human-readable format with context (units, timestamps, equipment ID)

- Contemporaneous: Data recorded at the time of the activity (real-time historian, no post-hoc entry)

- Original: Source data preserved in original format; copies clearly identified (historian as system of record)

- Accurate: Calibrated instruments, validated calculations, error-checked data entry

- +Complete: No selective data deletion; all data including out-of-spec results retained

- +Consistent: Timestamps synchronized (IEEE 1588 PTP); data formats standardized across systems

- +Enduring: Data retained per regulatory retention schedule (minimum 2 years past device expected life for MDR)

- +Available: Data accessible for review throughout its retention period; migration plan for format obsolescence

# 15. Cybersecurity Architecture

## 15.1 Defense-in-Depth Strategy

The cybersecurity architecture follows IEC 62443 zone/conduit model with defense-in-depth. Key design elements:

- Network Segmentation: Air-gapped Level 0-1 from IT; DMZ with data diode for unidirectional data flow from OT to IT where feasible

- Zero Trust: No implicit trust based on network location; all access authenticated and authorized per least privilege

- Endpoint Protection: Application whitelisting on all OT servers (e.g., CyberArk/Trellix) rather than signature-based AV

- Patch Management: OT-specific patch management with vendor-validated patches applied during maintenance windows

- Monitoring: OT-specific IDS/IPS (Claroty or Nozomi Networks) monitoring all OT network traffic for anomalous behavior

- Incident Response: OT-specific incident response plan with defined playbooks for common scenarios (ransomware, unauthorized access, equipment compromise)

- Backup & Recovery: Immutable backups (air-gapped or WORM) with tested recovery procedures; RPO < 1 hour, RTO < 4 hours for critical systems

## 15.2 Identity & Access Management

- Centralized Identity: Active Directory for IT/OT with dedicated OT OU and separate privileged access management

- Multi-Factor Authentication: Required for all Level 3+ access and all remote access to OT systems

- Privileged Access: CyberArk or equivalent PAM for all administrative access to OT systems; session recording for audit

- Badge-Based OT Access: RFID badge required for PLC programming terminals and HMI engineering access

# 16. Scaling Model: Line to Plant to Enterprise

## 16.1 Horizontal Scaling (Adding Lines)

Each manufacturing line is deployed as a self-contained module. Adding a new line follows this process:

- Clone baseline configuration (PLC programs, DCS templates, network config) from validated golden template

- Deploy physical infrastructure (sensors, PLCs, network switches, gateways) per Bill of Materials

- Configure line-specific parameters (line ID, equipment tags, network addresses)

- Execute IQ: Verify installation against specification

- Execute OQ: Verify operation using standard test protocols adapted from baseline

- Execute PQ: Run production qualification batches

- Integrate into plant-level DCS, historian, MES

Target: New line deployment in 8-12 weeks from equipment installation to PQ completion, leveraging reusable qualification packages from baseline.

## 16.2 Vertical Scaling (Plant Replication)

Deploying the digital footprint to a new Hollister plant:

- Plant Assessment: Evaluate existing infrastructure, regulatory environment, and local requirements

- Plant Template Deployment: Deploy plant-level infrastructure (server room, network core, security systems) from plant template

- Line-by-Line Deployment: Deploy manufacturing lines using the baseline line template

- Plant Integration: Connect to enterprise data lake, supply chain integration bus, and corporate IT services

- Site Qualification: Plant-level IQ/OQ/PQ covering inter-system integration and facility-wide functions

## 16.3 Enterprise Integration (Supply Chain)

The supply chain digital footprint connects all plants through:

- Enterprise Data Lake: Aggregated production, quality, and supply chain data from all plants

- Digital Twin (Enterprise): Federated digital twin models for each plant, connected for supply chain simulation

- Supply Chain Control Tower: Real-time visibility across all plants, warehouses, and logistics partners

- Unified Quality Dashboard: Cross-plant quality metrics, CAPA tracking, and regulatory submission readiness

- Master Data Hub: Centralized product master, material master, and equipment master synchronized across all plants

# 17. Implementation Roadmap

## 17.1 Phased Deployment Plan

| Phase | Duration | Scope | Key Deliverables |
| --- | --- | --- | --- |
| Phase 0: Foundation | Months 1-3 | Architecture validation, vendor selection, standards development | Approved architecture, vendor contracts, PLC/DCS programming standards, qualification master plan |
| Phase 1: Pilot Line | Months 4-9 | Single manufacturing line at Ballina (S1-S7) fully instrumented | Baseline line deployed, IQ/OQ complete, interim PLM operational, MES integration validated |
| Phase 2: Pilot PQ & Optimization | Months 10-14 | PQ execution, performance optimization, lessons learned | PQ complete, golden template validated, deployment playbook refined, MOD capability demonstrated |
| Phase 3: Ballina Full Deployment | Months 15-24 | Remaining 5-7 lines at Ballina + plant infrastructure | All Ballina lines operational, plant historian, security ops center, full environmental monitoring |
| Phase 4: Second Plant | Months 18-30 | Replicate to second plant (overlapping with Phase 3) | Second plant operational using refined templates; cross-plant analytics operational |
| Phase 5: Enterprise Rollout | Months 24-48 | All remaining plants + supply chain integration | Full enterprise digital footprint; supply chain visibility; permanent PLM selection and migration |

## 17.2 Investment Estimate (Order of Magnitude)

The following provides a rough order of magnitude (ROM) investment estimate for the baseline pilot line and subsequent scaling:

| Component | Pilot Line (1 Line) | Full Plant (8 Lines) | Notes |
| --- | --- | --- | --- |
| PLCs & Safety Controllers | $350K - $500K | $3.2M - $4.5M | Includes I/O modules, communication modules, racks |
| DCS/SCADA Software | $150K - $250K | $400K - $600K | PlantPAx licenses, historian, HMI servers |
| Sensors & Instrumentation | $400K - $600K | $3.5M - $5.0M | All sensor categories per architecture |
| Camera Systems (All Types) | $200K - $350K | $1.5M - $2.5M | Machine vision, process, security |
| IoT Gateways & Edge Compute | $100K - $180K | $800K - $1.2M | Station, line, and plant-level gateways |
| Server Room Infrastructure | $0 (use existing) | $600K - $900K | Servers, SAN, network core (plant-level) |
| Network Infrastructure | $150K - $250K | $800K - $1.2M | Switches, firewalls, cabling, Wi-Fi |
| Interim PLM | $50K - $100K | $100K - $200K | Aras Innovator (open source core + services) |
| Systems Integration | $500K - $800K | $2.5M - $4.0M | Engineering, programming, configuration |
| Qualification (IQ/OQ/PQ) | $300K - $500K | $1.5M - $2.5M | Protocol development, execution, documentation |
| TOTAL (ROM) | $2.2M - $3.5M | $14.9M - $22.6M | Excludes manufacturing equipment itself |

# 18. Appendices

## Appendix A: Acronym Reference

| Acronym | Definition |
| --- | --- |
| BMS | Building Management System |
| BOM | Bill of Materials |
| CAPA | Corrective and Preventive Action |
| CMDB | Configuration Management Database |
| CPP | Critical Process Parameter |
| CQA | Critical Quality Attribute |
| CTQ | Critical to Quality |
| DCS | Distributed Control System |
| DHF | Design History File |
| DMR | Device Master Record |
| DMZ | Demilitarized Zone |
| DLR | Device Level Ring |
| EBR | Electronic Batch Record |
| ECO | Engineering Change Order |
| EMS | Environmental Monitoring System |
| FAT | Factory Acceptance Testing |
| FRS | Functional Requirements Specification |
| GAMP | Good Automated Manufacturing Practice |
| HMI | Human-Machine Interface |
| IQ | Installation Qualification |
| MES | Manufacturing Execution System |
| MOD | Manufacturing on Demand |
| MOM | Manufacturing Operations Management |
| OEE | Overall Equipment Effectiveness |
| OQ | Operational Qualification |
| OT | Operational Technology |
| PAT | Process Analytical Technology |
| PLM | Product Lifecycle Management |
| PQ | Performance Qualification |
| PTP | Precision Time Protocol |
| RTLS | Real-Time Location System |
| SAT | Site Acceptance Testing |
| SCADA | Supervisory Control and Data Acquisition |
| SPC | Statistical Process Control |
| URS | User Requirements Specification |
| V&V | Verification and Validation |

## Appendix B: Key Vendor Summary

| Domain | Primary Vendor | Product/Platform | Role |
| --- | --- | --- | --- |
| PLCs | Rockwell Automation | ControlLogix 5580 / CompactLogix 5380 / GuardLogix | Primary automation platform |
| DCS/SCADA | Rockwell Automation | PlantPAx 5.0 / FactoryTalk View SE | Supervisory control and monitoring |
| Process Sensors | Endress+Hauser | Various (iTEMP, Promass, Liquiline) | Standardized process instrumentation |
| Machine Vision | Cognex | In-Sight 9000 / DataMan 475V | Quality inspection and identification |
| Precision Measurement | Keyence | LJ-X8000 / LS-9030 | Dimensional measurement and profiling |
| Cameras (Facility) | Axis Communications | P/M/Q series cameras | Process monitoring and security |
| Vibration/Predictive | Fluke / PCB Piezotronics | 3561 FC / 356A45 | Machine health monitoring |
| Environmental Monitoring | Vaisala / TSI | HMT330 / AeroTrak 9310 | Clean room environmental monitoring |
| IoT Gateways | Advantech / Moxa | UNO-2484G / UC-8200 | Edge data aggregation |
| Edge/Server Compute | Dell Technologies | PowerEdge R760 / PowerStore | On-premise compute and storage |
| Cloud Platform | Microsoft Azure | IoT Hub, Data Lake, ML, Digital Twins | Enterprise analytics and cloud extension |
| Network (OT) | Rockwell (Stratix/Cisco) | Stratix 5700/5400 | Industrial network switching |
| Network (IT) | Cisco | Catalyst 9300/9500 | Enterprise network infrastructure |
| OT Security | Claroty or Nozomi Networks | Platform for OT visibility | OT-specific threat detection |
| Interim PLM | Aras | Innovator | Product lifecycle management (interim) |
| Calibration Mgmt | Beamex / Blue Mountain | CMX / RAM | Metrology and calibration management |

--- End of Document ---

This document is a living architecture specification. It will be updated as the design progresses through Phase 0 detailed engineering and vendor selection. All recommendations are subject to final vendor evaluation, site assessment, and regulatory review.